## Imperial
[5 empty] | ROUND DUCT ORDER SHEET | [18 empty] | 8
Straight Duct with 45° Lateral Tap
TAP SPECIFICATIONS
[6 empty] | -D1- | -L1- |  | -D1- | -D2- | -D3- |  |  | -L2- |  | -L3- | -D3- | -A1-
[6 empty] | DUCT | DUCT |  | RING | RING | TAP |  |  | LOCATE |  | TAP | RING | TAP
FITTING NUMBER |  |  |  | QTY |  | DIA | LENGTH |  | TYPE | TYPE | DIA |  |  | FROM D1 |  | LENGTH | TYPE | ANGLE |  |  | REMARKS
"L1" MIN = ( "D3" X 1.414 ) + "L2 MIN (101.6)" + "L4 MIN" | [12 empty] | *MIN LENGTH FOR "L3" AND "L4"
( SEE MIN LENGTH CHART ABOVE FOR "L4" ) | [12 empty] | "D1" | [5 empty] | "L3" |  |  |  | "L4"
"L1" MAX = 96-1/4" (2444.8) | [12 empty] | 4" (101.6)-48" (1219.2) | [5 empty] | 6" (152.4) MIN |  |  |  | 4" (101.6) MIN
"D3" MAX = 60" (1524.0) | [12 empty] | 50" (1270.0)-58" (1473.2) | [5 empty] | 7" (177.8) MIN |  |  |  | 4" (101.6) MIN
LATERAL TAP GREATER THAN 60" (1524.0) [ "D3" ] | [12 empty] | 60" (1524.0)-94" (2387.6) | [5 empty] | 8" (203.2) MIN |  |  |  | 5" (127.0) MIN
REQUIRES 2 PIECE DESIGN AND ENGINEERING REVIEW | [12 empty] | 96" (2348.4)-120" (3048.0) | [5 empty] | 10-1/2" (266.7) MIN |  |  |  | 6" (152.4) MIN
STANDARD DUCT LENGTHS ("L1")
RING | DIAMETER |  |  |  | "L1"=4' (1219.2) |  |  | "L1"=8' (2438.4) |  |  |  | RING |  |  | DIAMETER |  |  |  |  | "L1"=4' (1219.2) |  | "L1"=8' (2438.4)
EZ/SC | 4" (101.6) & 6" (152.4) |  |  |  | 47.25" (1200.5) |  |  | NA |  |  |  | BI |  |  | 8" (203.2) TO 48" (1219.2) |  |  |  |  | 47.25" (1200.5) |  | 95.25" (2419.35)
EZ/SC | 8" (203.2) TO 14" (355.6) |  |  |  | 47.25" (1200.5) |  |  | 95.25" (2419.35) |  |  |  | SS |  |  | 16" (406.4) TO 48" (1219.2) |  |  |  |  | 47.25" (1200.5) |  | 95.25" (2419.35)
BI | 4" (101.6) & 6" (152.4) |  |  |  | 47.25" (1200.5) |  |  | NA |  |  |  | BI/SS |  |  | 50" (1270) TO 120" (3048) |  |  |  |  | 46.75" (1187.45) |  | 94.75" (2406.65)
NOTES: |  | 1 | SEE THE STANDARDS SECTION OF THE PRODUCT CATALOG FOR INFORMATION ABOUT | [16 empty] | DUCT JOINT / RING TYPE
DUCT GAUGE, RING MECHANICAL SPECS, HARDWARE AND GASKETS.
|  | 2 | OPTION: CUSTOM LENGTH | [16 empty] | EZ | EZ CLAMP
|  | 3 | OPTION: RAW END | [17 empty] | 4"Ø-14"Ø (101.6-355.6)
|  | 4 | OPTION: MULTIPLE / OFFSET TAPS (SEE MULTIPLE TAP SHEET) | [16 empty] | SC | STAINLESS CAST RING
|  | 5 | DUCT GREATER THAN 84" DIA. (2133.6mm) REQUIRES FAB-TECH ENGINEERING REVIEW | [17 empty] | 4"Ø-14"Ø (101.6-355.6)
|  |  | AND APPROVAL. | [16 empty] | BI | BLACK IRON ANGLE RING
|  | 6 | OUR RECOMMENDATION IS TO ADD TAPS TO STANDARD 4' (1219.2) AND 8' (2438.4) DUCT | [17 empty] | 4"Ø-120"Ø (101.6-3048.0)
|  |  | WHEN POSSIBLE - TAP DIMENSIONS SHOWN ARE MINS. LONGER THAN STANDARD | [16 empty] | SS | STAINLESS ANGLE RING
|  |  | LENGTHS AND/OR HIGHER SYSTEM PRESSURE MAY REQUIRE ADDITIONAL STIFFENERS PER | [17 empty] | 16"Ø-120"Ø (406.4-3048.0)
SMACNA, CONTACT FAB-TECH FOR SPECIFIC GUIDELINES.
|  | 7 | ALL DUCT FITTINGS WITH STANDARD FAB-TECH CONNECTIONS INCLUDE GASKETS AND
CLAMPS OR HARDWARE AS REQUIRED FOR INSTALLATION.
METRIC EQUIVALENTS ARE SHOWN IN PARENTHESIS & ITALICS (MILLIMETERS OR AS NOTED)
REMARKS:
COMPANY / JOB REFERENCE:
FAB-TECH, Inc. / Tel: 802-655-8800 / Fax: 802-655-8804 / www.fabtechinc.com / info@fabtechinc.com
© COPYRIGHT 2023 FAB-TECH, INC. REV: 01/18/23 RND008BD | [23 empty] | 8

## Metric
[5 empty] | ROUND DUCT ORDER SHEET | [18 empty] | 8
Straight Duct with 45° Lateral Tap
TAP SPECIFICATIONS
[6 empty] | -D1- | -L1- |  | -D1- | -D2- | -D3- |  |  | -L2- |  | -L3- | -D3- | -A1-
[6 empty] | DUCT | DUCT |  | RING | RING | TAP |  |  | LOCATE |  | TAP | RING | TAP
FITTING NUMBER |  |  |  | QTY |  | DIA | LENGTH |  | TYPE | TYPE | DIA |  |  | FROM D1 |  | LENGTH | TYPE | ANGLE |  |  | REMARKS
"L1" MIN = ( "D3" X 1.414 ) + "L2 MIN (101.6)" + "L4 MIN" | [12 empty] | *MIN LENGTH FOR "L3" AND "L4"
( SEE MIN LENGTH CHART ABOVE FOR "L4" ) | [12 empty] | "D1" | [5 empty] | "L3" |  |  |  | "L4"
"L1" MAX = 96-1/4" (2444.8) | [12 empty] | 4" (101.6)-48" (1219.2) | [5 empty] | 6" (152.4) MIN |  |  |  | 4" (101.6) MIN
"D3" MAX = 60" (1524.0) | [12 empty] | 50" (1270.0)-58" (1473.2) | [5 empty] | 7" (177.8) MIN |  |  |  | 4" (101.6) MIN
LATERAL TAP GREATER THAN 60" (1524.0) [ "D3" ] | [12 empty] | 60" (1524.0)-94" (2387.6) | [5 empty] | 8" (203.2) MIN |  |  |  | 5" (127.0) MIN
REQUIRES 2 PIECE DESIGN AND ENGINEERING REVIEW | [12 empty] | 96" (2348.4)-120" (3048.0) | [5 empty] | 10-1/2" (266.7) MIN |  |  |  | 6" (152.4) MIN
STANDARD DUCT LENGTHS ("L1")
RING | DIAMETER |  |  |  | "L1"=4' (1219.2) |  |  | "L1"=8' (2438.4) |  |  |  | RING |  |  | DIAMETER |  |  |  |  | "L1"=4' (1219.2) |  | "L1"=8' (2438.4)
EZ/SC | 4" (101.6) & 6" (152.4) |  |  |  | 47.25" (1200.5) |  |  | NA |  |  |  | BI |  |  | 8" (203.2) TO 48" (1219.2) |  |  |  |  | 47.25" (1200.5) |  | 95.25" (2419.35)
EZ/SC | 8" (203.2) TO 14" (355.6) |  |  |  | 47.25" (1200.5) |  |  | 95.25" (2419.35) |  |  |  | SS |  |  | 16" (406.4) TO 48" (1219.2) |  |  |  |  | 47.25" (1200.5) |  | 95.25" (2419.35)
BI | 4" (101.6) & 6" (152.4) |  |  |  | 47.25" (1200.5) |  |  | NA |  |  |  | BI/SS |  |  | 50" (1270) TO 120" (3048) |  |  |  |  | 46.75" (1187.45) |  | 94.75" (2406.65)
NOTES: |  | 1 | SEE THE STANDARDS SECTION OF THE PRODUCT CATALOG FOR INFORMATION ABOUT | [16 empty] | DUCT JOINT / RING TYPE
DUCT GAUGE, RING MECHANICAL SPECS, HARDWARE AND GASKETS.
|  | 2 | OPTION: CUSTOM LENGTH | [16 empty] | EZ | EZ CLAMP
|  | 3 | OPTION: RAW END | [17 empty] | 4"Ø-14"Ø (101.6-355.6)
|  | 4 | OPTION: MULTIPLE / OFFSET TAPS (SEE MULTIPLE TAP SHEET) | [16 empty] | SC | STAINLESS CAST RING
|  | 5 | DUCT GREATER THAN 84" DIA. (2133.6mm) REQUIRES FAB-TECH ENGINEERING REVIEW | [17 empty] | 4"Ø-14"Ø (101.6-355.6)
|  |  | AND APPROVAL. | [16 empty] | BI | BLACK IRON ANGLE RING
|  | 6 | OUR RECOMMENDATION IS TO ADD TAPS TO STANDARD 4' (1219.2) AND 8' (2438.4) DUCT | [17 empty] | 4"Ø-120"Ø (101.6-3048.0)
|  |  | WHEN POSSIBLE - TAP DIMENSIONS SHOWN ARE MINS. LONGER THAN STANDARD | [16 empty] | SS | STAINLESS ANGLE RING
|  |  | LENGTHS AND/OR HIGHER SYSTEM PRESSURE MAY REQUIRE ADDITIONAL STIFFENERS PER | [17 empty] | 16"Ø-120"Ø (406.4-3048.0)
SMACNA, CONTACT FAB-TECH FOR SPECIFIC GUIDELINES.
|  | 7 | ALL DUCT FITTINGS WITH STANDARD FAB-TECH CONNECTIONS INCLUDE GASKETS AND
CLAMPS OR HARDWARE AS REQUIRED FOR INSTALLATION.
METRIC EQUIVALENTS ARE SHOWN IN PARENTHESIS & ITALICS (MILLIMETERS OR AS NOTED)
REMARKS:
COMPANY / JOB REFERENCE:
FAB-TECH, Inc. / Tel: 802-655-8800 / Fax: 802-655-8804 / www.fabtechinc.com / info@fabtechinc.com
© COPYRIGHT 2023 FAB-TECH, INC. REV: 01/18/23 RND008BD | [23 empty] | 8