## Imperial
[5 empty] | ROUND DUCT ORDER SHEET |  |  |  | 27
50" (1270.0) & Larger Reinforced Heavy Duty Industrial Damper (HVD)
SPECIFICATIONS
DIFFERENTIAL PRESSURE: 10"WG (2,488 Pa)
BODY: COATED 1/4" (6.35) SS
BODY LENGTH: 10" (254.0)
OPTION: AVAIL TO 120" (3048.0) DIA W/
ENGINEERING REVIEW
COATING: PERMASHIELD FLUOROPOLYMER
BARRIER COATING
JOINING SYSTEM: STICH WELDED STAINLESS
STEEL VAN STONE RINGS
OPTION: CUSTOM HOLE PATTERN
MOUNTING HOLES: STRADDLE VERTICAL
CENTERLINE
BLADE: 3/8" (9.5) COATED REINFORCED
STAINLESS STEEL
BLADE STOPS: WELDED
AXLES: DUAL SHAFT 1.85Ø (47.0) SS
AXLE SEALS: LIQUID TIGHT
SLEEVE BEARINGS: THERMOPLASTIC
ACTUATOR: GEAR ACTUATOR W/ LOCK OUT
OPTION: CUSTOM ACTUATOR MOUNTING KIT
OPTION: ELECTRIC ACTUATOR
OPTION: PNEUMATIC ACTUATOR
PNEUMATIC ACTUATED DAMPERS
HYTORK ACTUATOR STANDARD
XL45 - UP TO 20" (508.0)
XL280 - 21" (533.4) TO 48" (1219.2)
XL425 - 49" (1244.6) TO 94" (2387.6)
LOCKOUT: 1/2­­° INTERVALS
BLADE OPENS: CCW
OPEN/CLOSE TORQUE: 1600 in-lb (180.8 N-m) RECOMMENDED MIN
INDICATE
[6 empty] | -D1- | CUSTOM RING
[6 empty] | DUCT | IF REQUIRED
FITTING NUMBER |  |  |  | QTY |  | DIA | D1 OR D2 | REMARKS
NOTES: | 1 |  | ALL DUCT FITTINGS WITH STANDARD FAB-TECH CONNECTIONS INCLUDE GASKETS AND
CLAMPS OR HARDWARE AS REQUIRED FOR INSTALLATION.
METRIC EQUIVALENTS ARE SHOWN IN PARENTHESIS & ITALICS (MILLIMETERS OR AS NOTED)
REMARKS:
COMPANY / JOB REFERENCE:
FAB-TECH, Inc. / Tel: 802-655-8800 / Fax: 802-655-8804 / www.fabtechinc.com / info@fabtechinc.com
© COPYRIGHT 2023 FAB-TECH, INC. REV: 09/11/23 RND027BE | [8 empty] | 27

## Metric
[5 empty] | ROUND DUCT ORDER SHEET |  |  |  | 27
50" (1270.0) & Larger Reinforced Heavy Duty Industrial Damper (HVD)
SPECIFICATIONS
DIFFERENTIAL PRESSURE: 10"WG (2,488 Pa)
BODY: COATED 1/4" (6.35) SS
BODY LENGTH: 10" (254.0)
OPTION: AVAIL TO 120" (3048.0) DIA W/
ENGINEERING REVIEW
COATING: PERMASHIELD FLUOROPOLYMER
BARRIER COATING
JOINING SYSTEM: STICH WELDED STAINLESS
STEEL VAN STONE RINGS
OPTION: CUSTOM HOLE PATTERN
MOUNTING HOLES: STRADDLE VERTICAL
CENTERLINE
BLADE: 3/8" (9.5) COATED REINFORCED
STAINLESS STEEL
BLADE STOPS: WELDED
AXLES: DUAL SHAFT 1.85Ø (47.0) SS
AXLE SEALS: LIQUID TIGHT
SLEEVE BEARINGS: THERMOPLASTIC
ACTUATOR: GEAR ACTUATOR W/ LOCK OUT
OPTION: CUSTOM ACTUATOR MOUNTING KIT
OPTION: ELECTRIC ACTUATOR
OPTION: PNEUMATIC ACTUATOR
PNEUMATIC ACTUATED DAMPERS
HYTORK ACTUATOR STANDARD
XL45 - UP TO 20" (508.0)
XL280 - 21" (533.4) TO 48" (1219.2)
XL425 - 49" (1244.6) TO 94" (2387.6)
LOCKOUT: 1/2­­° INTERVALS
BLADE OPENS: CCW
OPEN/CLOSE TORQUE: 1600 in-lb (180.8 N-m) RECOMMENDED MIN
INDICATE
[6 empty] | -D1- | CUSTOM RING
[6 empty] | DUCT | IF REQUIRED
FITTING NUMBER |  |  |  | QTY |  | DIA | D1 OR D2 | REMARKS
NOTES: | 1 |  | ALL DUCT FITTINGS WITH STANDARD FAB-TECH CONNECTIONS INCLUDE GASKETS AND
CLAMPS OR HARDWARE AS REQUIRED FOR INSTALLATION.
METRIC EQUIVALENTS ARE SHOWN IN PARENTHESIS & ITALICS (MILLIMETERS OR AS NOTED)
REMARKS:
COMPANY / JOB REFERENCE:
FAB-TECH, Inc. / Tel: 802-655-8800 / Fax: 802-655-8804 / www.fabtechinc.com / info@fabtechinc.com
© COPYRIGHT 2023 FAB-TECH, INC. REV: 09/11/23 RND027BE | [8 empty] | 27