## Sheet1
[5 empty] | ROUND DUCT ORDER SHEET | [13 empty] | 12
Reducers
[6 empty] | -D1- | -D2- |  | -L1- | -L2- | -L3- |  | -D1- | -D2-
[6 empty] | DUCT | DUCT |  | DUCT | TAPER | CENTER |  | RING | RING
FITTING NUMBER |  |  | QTY |  |  | DIA | DIA |  | LENGTH | LENGTH | OFFSET |  | TYPE | TYPE | REMARKS
ECCENTRIC | [7 empty] | CONCENTRIC | [6 empty] | MIN "L4" / "L5"
AMOUNT OF REDUCTION |  |  |  | MINIMUM |  |  |  | AMOUNT OF REDUCTION |  |  |  | MINIMUM |  |  | DUCT DIAMETER |  |  | MINIMUM
"D1" minus "D2" |  |  |  | "L2" |  |  |  | "D1" minus "D2" |  |  |  | "L2" |  |  | "D1" or "D2" |  |  | "L4 or "L5"
6" (152.4) AND LESS |  |  |  | 12" (304.8) |  |  |  | 9" (228.6) AND LESS |  |  |  | 12" (304.8) |  |  | 4" (101.6) TO 58" (1473.2) |  |  | 3" (76.2)
7" (177.8) TO 9" (288.6) |  |  |  | 18" (457.2) |  |  |  | 10" (254.0) TO 14" (355.6) |  |  |  | 18" (457.2) |  |  | 60" (1524.0) TO 94" (2387.6) |  |  | 4" (101.6)
10" (254.0) TO 13" (330.2) |  |  |  | 24" (609.6) |  |  |  | 15" (381.0) TO 19" (482.6) |  |  |  | 24" (609.6) |  |  | 96" (2438.4) TO 120" (3048.0) |  |  | 5" (127.0)
14" (355.6) TO 17" (431.8) |  |  |  | 30" (762.0) |  |  |  | 20" (508.0) TO 24" (609.6) |  |  |  | 30" (762.0)
DUCT JOINT / RING TYPE
[16 empty] | EZ | EZ CLAMP
NOTES: | 1 | SEE THE STANDARDS SECTION OF THE PRODUCT CATALOG FOR INFORMATION ABOUT | [14 empty] | 4"Ø-14"Ø (101.6-355.6)
|  | DUCT GAUGE, RING MECHANICAL SPECS, HARDWARE AND GASKETS. | [13 empty] | SC | STAINLESS CAST RING
| 2 | OPTION: CUSTOM LENGTHS AVAILABLE | [14 empty] | 4"Ø-14"Ø (101.6-355.6)
| 3 | DUCT GREATER THAN 84" (2133.6mm) REQUIRES FAB-TECH ENGINEERING REVIEW | [13 empty] | BI | BLACK IRON ANGLE RING
|  | AND APPROVAL. | [14 empty] | 16"Ø-120"Ø (406.4-3048.0)
| 4 | ALL DUCT FITTINGS WITH STANDARD FAB-TECH CONNECTIONS INCLUDE GASKETS AND | [13 empty] | SS | STAINLESS ANGLE RING
|  | CLAMPS OR HARDWARE AS REQUIRED FOR INSTALLATION. | [14 empty] | 16"Ø-120"Ø (406.4-3048.0)
METRIC EQUIVALENTS ARE SHOWN IN PARENTHESIS & ITALICS (MILLIMETERS OR AS NOTED)
REMARKS:
COMPANY / JOB REFERENCE:
FAB-TECH, Inc. / Tel: 802-655-8800 / Fax: 802-655-8804 / www.fabtechinc.com / info@fabtechinc.com
© COPYRIGHT 2023 FAB-TECH, INC. REV: 03/20/24 RND012BE | [18 empty] | 12